## 1. Asset Categories & Req Spec
Data Collection Requirements
Asset Group | Asset Type ("Maintainable" Assets) | Asset Type Acronyms | Maximo Number | Description | Parent Description | Location | Asset Type | Supplier | Manufacturer | Model | Serial No. | Electrical Branch (Electrical) | Fed From (Electrical) | Pressure Vessel | Manufacturers Instruction Manuals | Installation/Substantial Completion Date | Warranty End Date | Warranty Certificate | Shop Drawings (Aproved)
ARCHITECTURAL
Architectural | Automatic Door | ADR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Architectural | Floor Drain | FD |  | Y | Y | Y | [9 empty] | Y |  |  | Y | Design Data (inc. in Registry)
Architectural | Guardrails | GR |  | Y | Y | Y | [9 empty] | Y |  |  | Y | Construction Data
Architectural | Overhead Door | OHDR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Architectural | Roof | ROOF |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Architectural | Roof Drain | RD |  | Y | Y | Y | [12 empty] | Y
CIVIL
Civil | Manhole | MH | Y | Y | Y | Y | Y | [11 empty] | Y
Civil | Stormwater Interceptor | STINT | Y | Y | Y | Y | Y | Y | Y | Y | [5 empty] | Y | Y |  | Y
ELECTRICAL
Electrical | Battery Charger | BATCHRG | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Capacitor | CAP | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Disconnect Switch | DS | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Distribution Panel | DP | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Fuel Oil Pump | FOP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Electrical | Fuel Oil Tank | FOT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Electrical | Generator | GEN | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Electrical | Generator Batteries | GENBAT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Electrical | Heat Trace | HT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Electrical | High Voltage Distribution Bus | HVBUS | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | High Voltage Protective Relay | HVPR | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Lighting Control Panel | LCP | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Load Shed Contactor | LSC | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Main Circuit Breaker | MCB | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Main Distribution Panel | MDP | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Motor Control Centre | MCC | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Panel Board | PNL | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Power Distribution Center | PDC | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Public Address System | PA | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Electrical | Reactor Bank | RB | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Electrical | Safety Switch | SSW | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Substation | SUB | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Switch Board | SWBD | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Switchgear | SWG | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Transfer Switch | TSW | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Transformer | TX | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Uniterruptible Power System | UPS | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
Electrical | Variable Frequency/Speed Drive | VSD | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y | Y |  | Y | Y | Y | Y | Y
ELEVATORS
Elevators | Conveyor | CONV | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Elevators | Dumbwaiter | DUMB | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Elevators | Elevator | ELEV | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Elevators | Escalator | ESC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Elevators | Monorail | MONO | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Elevators | Scissor Lift | SL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HOSPITAL EQUIPMENT
Hospital Equipment | Addressograph | ADG | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Automatic Endoscope Reprocessor | AER | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Automatic Straining Equipment | ASE |  | Y | Y | Y | [9 empty] | Y | Y | Y | Y
Hospital Equipment | Bed Pan Disinfector | BPD | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Biosafety Cabinets | BSC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Cage Washer | CAGEW | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Cart Washer | CARTW | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Clocks | CLK |  | Y | Y | Y |  |  | Y | Y |  |  |  |  | Y | Y | Y |  | Y
Hospital Equipment | Code Blue System | CODEB | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Detergent Dosing Dispenser | DOSE | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Dialysis Water System | DIA | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Dishwasher | DISH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Dryer Cabinet | DC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Dust Extraction System | DUST | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Electric Drinking Fountain | EDF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Bed | EB | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Emergency Shower | ES | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Emergency Shower And Eyewash Unit | ESEW | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Eyewash Station | EW | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Freezer | FRZ | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Fume Hood | FH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Garbage Chute | GC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Grease Interceptor | GI | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Helipad | HPD | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Ice Machine | IM | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Incubator (Sterilizer) | INC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Instrument Washer | INSTW | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Kitchen Appliance | APP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Ladder | LAD |  | Y | Y | Y | [9 empty] | Y |  | Y | Y
Hospital Equipment | Laundry Dryer | LDRY | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Laundry Washer | LWASH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Loading Dock Leveler | ED | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Macerators | MAC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Mowing Equipment | MOWE | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Nurse Call System | NC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Nurse racks | NR |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Nurse phone | NPH |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Nurse Calling - Bed Stations | BSTN |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Nurse Calling - Dome Light | DL |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Panic Station | PS |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Oven | OVEN | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Overhead Paging | OHP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Paging | PAGE | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Pasteurizer | PAST | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Patient Wandering | PW | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Plaster Trap | PT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Pool | POOL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Reach In Cooler | RIC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Refrigerator | FRDG | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Reverse Osmosis System | ROS | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Security Alarm | SA |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Steam Filter | STFLTR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Hospital Equipment | Steam Kettle | STMK | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Hospital Equipment | Steamer | STMR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Hospital Equipment | Sterilizer | STER | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Hospital Equipment | Tube Blower Motor | TUBEB | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Tube Station | TUBES | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Tube Transfer Unit | TUBET | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Ultrasonic Cleaner | USC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Vehicle | VEH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Waste Compactor | WSTC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Hospital Equipment | Waste Dumper | WSTD | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC
HVAC | Air Compressor | AC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Air Conditioning Condensing Unit | CU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Air Conditioning Unit | ACU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Air Curtain | ACUR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Air Dryer | AD | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Air Filter | AF | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Air Handling Unit | AHU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Air Receiver | AR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Air Separator | AS | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Air Tank | AT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Boiler | BLR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Building Automation System | BAS |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Chemical Feed Equipment | CFE | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Chemical Feed Tank | CFT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Chilled Water Heat Exchanger | CHWHEX | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Chilled Water Pump | CHWP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Chiller | CH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Chiller Condensor Pump | CCP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Coil | C | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Cold Deck | CD | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Compression Tank | CTK | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Computer Room A/C Unit | CRAC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Condensate Receiver | CONDR | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Condensate Tank | CONDT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Condensing Fan Unit | CONDF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Condensing Unit | CU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Controlled Pressure Environment | CPE |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | HVAC Cooler | COOL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Cooling Tower | CT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | De-Aerator | DA | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Dehumidifier | DHUM | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Duct Silencer | DSIL |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Economizer | ECON | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Exhaust Volume Control Box | EVCB |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
HVAC | Electric Duct Heater | EDH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Exhaust Fan | EF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Expansion Tank | ET | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Fan | F | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Fan Coil Unit | FCU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Flash Tank | FT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Force Flow Heater | FF |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Fume Hood Exhaust Fan | FHEF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Heat Exchanger | HEX | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
HVAC | Heat Pump | HP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Heat Recovery Unit | HRU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Hot Deck | HD | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Humidifier | HUM | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | HVAC Temperature Controllers | HVACTC |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | HVAC Temperature Detectors | HVACTD |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Isolation Monitor / Controls | IMC | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Isolation Room Exhaust Fan | IEF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Kitchen Exhaust Fan | KEF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Manual Dampers | DAMP |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Mixing Box | MB |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Motorized Dampers | DAMP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Negative Air Units | NAU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Pressure Relief Valve | PRV |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
HVAC | Pressurization Fan | PF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Radiant Heat Panel | RHP |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y |  |  | Y | Y
HVAC | Radiant Heating System | RHS |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Radiological Exhaust Fan | REF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Refrigerant Controller | REFC |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Refrigerant Detection System | REFD | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC | Return Fan | RF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Safety Valve | SV |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
HVAC | Stairwell Pressurization Fan | SPF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC: HVAC; Fan: Supply Air Intake; F: SAI; Y: Y; Y: Y; Y: Y |  |  |  | Y | Y |  | Y | Y
HVAC | Supply Fan | SF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Terminal Heating Unit | THU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Unit Heater | UH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC | Variable Air Volume Box | VAV | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
LIFE SAFETY
Life Safety | Carbon Monoxide Alarm Systems | COALRM | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | CO2 | CO2SEN | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | NO2 Sensor | NO2SEN | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Dry Pipe Sprinkler System | DPSS |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Duct Smoke Detector | DSD |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Emergency Lighting | EML | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Exit Light | EXL |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Alarm Annunciator | FAAN | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Alarm Flow Switch | FAFS |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Alarm Magnetic Door Holder | FAMAG |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Alarm Control Panels | FAPNL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y
Life Safety | Fire Alarm Speaker | FASP |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Life Safety | Fire alarm Visual and Strobe | FAV |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Life Safety | Fire Department Connection | FDC |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Doors | FDRS | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
HVAC: Life Safety; Fan: Fire Extinguisher; F: FEXT; Y: Y; Y: Y; Y: Y |  |  |  | Y | Y |  | Y | Y
Life Safety | Fire Hose Cabinet | FHC |  | Y | Y | Y |  | Y | Y | [6 empty] | Y | Y | Y | Y
Life Safety | Fire Hydrant | HYD | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Protection Backflow Preventor | FPBFP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y
Life Safety | Fire Protection Dry -Air Compressor | FPDAC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Life Safety | Fire Protection Water Pump | FPWP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Protection Water Storage Tank | FPWT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Life Safety | Fire Pump Automatic Transfer Switch | FPATS | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Pump Switch Gear | FPSW | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Sprinkler System | FSRP |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Suppression System (specialized) | FSUPP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Fire Switches | FASW | Y | Y | Y | Y | Y | Y | Y | Y | Y | [5 empty] | Y | Y | Y
Life Safety | Fire System Damper | FDAMP |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Life Safety | Gas Detector | GD | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Heat Detectors | HD |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y |  |  | Y | Y
Life Safety | Jockey Pump | JP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Kitchen Hood Fire Suppression | KHFS | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Pullstations | PS |  | Y | Y | Y |  | Y | Y | [5 empty] | Y | Y | Y | Y | Y
Life Safety | Standpipe | STP |  | Y | Y | Y |  | Y | Y | [5 empty] | Y | Y | Y | Y | Y
Fan: Warning Lights; F: WL; Y: Y; Y: Y; Y: Y; Y: Y; Y: Y |  |  |  | Y | Y | Y | Y | Y
Life Safety | Wet Pipe Sprinkler System | WPSS |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
MEDICAL AGV
Medical Gas | Liquid Nitrogen Tank | LNT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Medical Gas | Liquid Oxygen System Equipment | LOS | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Medical Gas | Liquid Oxygen Tank | LOT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Medical Gas | Medical Air Compressor | MAIRC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Medical Gas | Medical Air Dryer | MAIRD | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Medical Air Outlet | MAIRO |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Medical Gas/Vacuum Local Alarm Panel | MGASLA | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Medical Gas/Vacuum Master Alarm Panel | MGASMA | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Medical Vacuum Pump | MVACP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Nitrogen Cylinder Manifold | NCM | Y | Y | Y | Y | Y | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Medical Gas | Nitrous Oxide Cylinder Manifold | N2OCM | Y | Y | Y | Y | Y | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Medical Gas | Nitrous Oxide Equipment | NO2E | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Nitrous Oxide Outlet | N2OMO |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Oxygen Cylinder Manifold | O2CM | Y | Y | Y | Y | Y | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Medical Gas | Oxygen Outlet | O2MO |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Vacuum Outlet | MVACO |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Vacuum Tank | VACT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Medical Gas | Dental Vacuum | DVAC | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Medical Gas | High Press Nitro Equipment | HPN |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Medical Gas | Liquid Nitrogen System Equipment | LNS |  | Y | Y | Y |  | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
PATIENT CARE
Patient Care | Bed | BED | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Blanket Warmer | BW | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Carbon Dioxide Equipment | CO2E | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Commode | COMM |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Patient Care | Medical Suction Pump | MSP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Operating Room Table | ORT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Exam Light | EXML | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Or Light | ORL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Wheelchair | WHCH |  | Y | Y | Y |  | Y | Y | Y | [5 empty] | Y | Y | Y | Y
Patient Care | Mobile Patient Lift | MPL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Overhead Patient Lift | OHPL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Overhead Patient Lift Gantry | OHPLG | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Patient Lift Scale | PLS | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Stretcher | STRH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Surgical Booms | BOOM | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Patient Care | Tub Lift | TL | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
PLUMBING
Plumbing | Acid Netralization Tank | ANT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Backflow Preventer | BFP-TYPE | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Combination Fire And Domestic Water Tank | CWT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Condensate Pump | CONDP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | De-Ionized Water System | DIS | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Domestic Hot Water Expansion Tank | DHWET | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Domestic Hot Water Recirculation Pump | DHWRP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Domestic Hot Water Tank | DHWT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Domestic Water Bladder Tank | DWBT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Domestic Water Pressure Reducing Valve | DCWPRV | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Domestic Water Storage Tank | DWT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Elevator Sump Pump | ESP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Gas Fired Domestic Hot Water Heater | GFDWH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Glycol Pump | GLP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Heating Hot Water Pump | HHWP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Hose Bibb | HB |  | Y | Y | Y |  | Y | Y | [6 empty] | Y | Y | Y | Y
Plumbing | Hot Water Heater | HWH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Hydraulic Oil Pump | HOP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Hydraulic Oil Tank | HOT | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Irrigation Sprinkler System | IRR |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Plumbing | Pump | P | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Pump Station | PSTN | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Sand Filter | SDF | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y |  | Y | Y
Plumbing | Sanitary Sump Pump | SSP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Secondary Chilled Water Pump | CHWSP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Sediment Interceptor | SEDINT | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y |  |  | Y | Y
Plumbing | Steam Domestic Water Heater | SDWH | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Steam Trap | ST | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Plumbing | Storage Tank | STO | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  | Y | Y | Y | Y | Y | Y
Plumbing | Storm Sump Pump | STSP | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Valve | V |  | Y | Y | Y |  | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Plumbing | Water Filter | WF | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  |  | Y | Y | Y | Y | Y
Plumbing | Water Meter | WM | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
Plumbing | Water Treatment Package Unit | WTPU | Y | Y | Y | Y | Y | Y | Y | Y | Y |  |  |  | Y | Y | Y | Y | Y
HVAC: Plumbing; Fan: Scrub sink; Y: Y; Y: Y; Y: Y; Y: Y; Y: Y |  |  |  |  | Y | Y | Y | Y
SPECIALTY
Specialty | RTLS Telehealth Touchpad | TRTLS |  | Y | Y | Y |  | Y | Y | Y | [8 empty] | Y

## 2. System Acronyms
System Group | System | System Acronyms
ELECTRICAL
Electrical | Conditional Power | CNDTL
Electrical | Delayed Vital | DV
Electrical | High Voltage | HV
Electrical | Standby Power | SB
Electrical | Vital | V
HOSPITAL EQUIPMENT
Hospital Equipment | Code Blue System | CODEB
Hospital Equipment | Nurse Call System | NC
Hospital Equipment | Public Address System | PA
Hospital Equipment | Reverse Osmosis System | RO
HVAC
HVAC | Building Automation System | BAS
HVAC | Carbon Monoxide Alarm Systems | COALRM
HVAC | Controlled Pressure Environment | CPE
HVAC | Dust Extraction System | DUST
HVAC | Lab Air | LAIR
HVAC | Exhaust Air | EA
HVAC | Outdoor Air | OA
HVAC | Return Air | RA
HVAC | Supply Air | SA
LIFE SAFETY
Life Safety | Fire Protection | FP
Life Safety | Fire Alarm System | FAS
MEDICAL AIR, GAS AND VACUUM
Medical AGV | Medical Air | MAIR
Medical AGV | Medical Gas | MGAS
Medical AGV | Medical Vacuum | MVAC
PIPING SYSTEMS
Piping Systems | Chilled Water | CHW
Piping Systems | High Pressure Condensate | HPCOND
Piping Systems | Low Pressure condensate | LPCOND
Piping Systems | Domestic Cold Water Supply | DCWS
Piping Systems | Domestic Hot Water Supply | DHWS
Piping Systems | Domestic Hot Water Return | DHWR
Piping Systems | Heating Hot Water Supply | HHWS
Piping Systems | Heating Hot Water Return | HHWR
Piping Systems | Steam | STM
Piping Systems | Boiler Feedwater | BFW
Piping Systems | Boiler Purge | BP
Piping Systems | Breeching | BR
Piping Systems | Chilled Water Return | CHWR
Piping Systems | Chilled Water Supply | CHWS
Piping Systems | Condenser Drain | CDD
Piping Systems | Condenser Water Return | CR
Piping Systems | Condenser Water Supply | CS
Piping Systems | Constant High Temperature Return | CHTR
Piping Systems | Constant High Temperature Supply | CHTS
Piping Systems | Corrosion Resistant | CRV
Piping Systems | Diesel Exhaust | DE
Piping Systems | Dehumidification System | DHUM
Piping Systems | Domestic Cold Water | DCW
Piping Systems | Domestic Hot Water | DHW
Piping Systems | Domestic Hot Water Recirculation | DHWR
Piping Systems | Hydronic Glycol Condenser Water Return | HGLCDWR
Piping Systems | Hydronic Glycol Condenser Water Supply | HGLCDWS
Piping Systems | Irrigation | IRR
Piping Systems | Low Pressure Condensate | LPC
Piping Systems | Low Pressure Propane | LPG
Piping Systems | Low Pressure Steam (Pressure noted in kPa) | LPS‐kPa
Piping Systems | Low Temperature Water Return | LTWR
Piping Systems | Low Temperature Water Supply | LTWS
Piping Systems | Natural Gas | NATGAS
Piping Systems | Process 15W‐40 | P15W40
Piping Systems | Process 5W‐30 | P5W30
Piping Systems | Pumped Condensate | PC
Piping Systems | Process Chilled Water Return | PCWR
Piping Systems | Process Chilled Water Supply | PCWS
Piping Systems | Process ATF | PATF
Piping Systems | Process Hydraul56 | PHYD
Piping Systems | Fuel Oil Fill | FOF
Piping Systems | Fuel Oil Return Above Grade | FORA
Piping Systems | Fuel Oil Return Below Grade | FORB
Piping Systems | Fuel Oil Supply Above Grade | FOSA
Piping Systems | Fuel Oil Supply Below Grade | FOSB
Piping Systems | Fuel Oil Vent | FOV
Piping Systems | Fire Protection Other | FPO
Piping Systems | Fire Protection‐Pre‐Action | FPPA
Piping Systems | Fire Protection Dry | FPD
Piping Systems | Fire Protection Wet | FPW
Piping Systems | Footing Drain | FTG
Piping Systems | Gravity Condensate | GC
Piping Systems | Glycol Return | GLR
Piping Systems | Glycol Supply | GLS
Piping Systems | High Pressure Condensate | HPCOND
Piping Systems | High Pressure Drip | HPD
Piping Systems | High Pressure Steam (Pressure noted in kPa) | HPS‐kPa
Piping Systems | Heat Pump Hot Water Return | HPHWR
Piping Systems | Heat Pump Hot Water Supply | HPHWS
Piping Systems | Heating Water Return | HWR
Piping Systems | Heating Water Supply | HWS
Piping Systems | Humidification | H
Piping Systems | Hydronic Condenser Water Return | HCDWR
Piping Systems | Hydronic Condenser Water Supply | HCDWS
Piping Systems | Process Nuto32 | PNUT
Piping Systems | Process Piping Coolant | PPC
Piping Systems | Process Sanitary Above Grade | PSANA
Piping Systems | Process Sanitary Below Grade | PSANB
Piping Systems | Pumped Storm | PST
Piping Systems | Process Ventilation | PVEN
Piping Systems | Process Water Deionized | PDI
Piping Systems | Process Water | PW
Piping Systems | Refrigeration ‐ Liquid | REF(L)
Piping Systems | Refrigerant ‐ Vapour | REF(V)
Piping Systems | Rainwater Leader | RWL
Piping Systems | Sanitary Drainage Above Grade | SANA
Piping Systems | Sanitary Drainage Below Grade | SANB
Piping Systems | Sanitary Drainage Pumped | SANP
Piping Systems | Storm | STM
Piping Systems | Standpipe | ST
Piping Systems | Storm Drainage Above Grade | STRA
Piping Systems | Storm Drainage Below Grade | STRB
Piping Systems | Storm Drainage Pumped | STRP
Piping Systems | Steam Vent | SRV
Piping Systems | Tempered Water | TW
Piping Systems | Vent | V
Piping Systems | Weeping Tile | WT

## 3. Data Template (not for BIM)
CMMS Asset # (silver adhesive labels) | Asset Description | Parent Asset # | Location - Building | Location - Floor | Location - Room | Asset Type | Maintenance Tag # | Supplier | Manufacturer | Model | Serial Number | Electrical Branch (Electrical Distribution Assets only) | Fed from (Electrical Distribution Assets only) | Installation Date | Warranty Date | Pressure Vessel # | Document File Path | Additional Notes
| (e.g., VFD, Chilled Water Pump 6 (CHW-P-06-VFD) | (e.g., see Sample Hierarchies in tabs 4-7 for Guidance) | (e.g., Segal Building) | (e.g., 1st Floor) | (e.g., Rm 101) | (e.g., VARIABLE FREQUENCY DRIVE - see Tab 6) | (e.g., CHW-P-06-VFD, see tabs 2 and 3 for acronyms) | (e.g., ABB) | (e.g., ABB) | (e.g., ACH550) | (e.g., 2133702396) | (e.g., Vital) | (e.g., TX-V6B1) | (yyyy-mm-dd) | (yyyy-mm-dd) | (If applicable) | (See Tab 2 for required documents) | (if applicable)
Risk Categories - for reference
Boiler & PV
Building Envelope
Clinical Communication
Electrical Distribution System
Emergency Power
Isolation Rooms
Life Safety
Medical Air / Gas
Patient Lifts
Sterilizers
HVAC

## 4. Asset Hierarchy Sample
Sample Asset Hierarchy |  |  |  | Additional Level of Detail Required for "Child" Assets
Architectural |  |  |  | None
| Building Envelope |  |  | None
|  | Roof |  | None
|  | Windows |  | None
|  | Doors (Exterior) |  | None
|  |  | Doors - Automatic (Exterior) | List individual automatic doors (e.g., at entrances)
| Building Interior |  |  | None
|  | Paint |  | None
|  | Doors (Interior) |  | None
|  |  | Doors - Fire | List individual fire doors
|  |  | Doors - Automatic (Interior) | List individual automatic doors (e.g., at entrances)
|  | Millwork |  | None
|  | Flooring |  | None
| Locks & Keys |  |  | None
|  | Locksets |  | None
|  |  | Cylinders | None
|  |  | Keys | None
Hospital Equipment |  |  |  | None
| Sterilizing Equipment |  |  | List anything not included in the following subcategories
|  | Sterilizers |  | List individual sterilizers
|  | Cartwashers |  | List individual cartwashers
| Bedpan Disinfectors |  |  | List individual bedpan disinfectors
| Kitchen Equipment |  |  | List anything not included in the following subcategories
|  | Refrigeration (Kitchen) |  | List individual kitchen refrigeration assets
|  | Dishwashers |  | List individual dishwashers assets here
|  | Steam Kettles |  | List individual steam kettle assets
|  | Steamers |  | List individual steamer assets
|  | Ovens |  | List individual oven assets
|  | Food Carts |  | List individual food cart assets
| Operating Room Equipment |  |  | List anything not included in the following subcategories
|  | Operating Room Tables |  | List individual operating room tables
|  | Operating Room Lights |  | List individual operating room lights
| Patient Lifts |  |  | None
|  | Ceiling |  | List individual ceiling lifts
|  | Mobile |  | List individual mobile lifts
| Carts |  |  | None
| Wheel Chairs |  |  | None
| Beds and Stretchers |  |  | None
|  | Beds |  | List individual beds
|  | Stretcher |  | List individual stretchers
| Blanket Warmer System |  |  | List individual blanket warmer cabinets
| Fume Hoods |  |  | List individual fume hoods
| Scale System |  |  | None
| Waste Handling |  |  | None
|  | Compactors |  | List individual compactors
|  | Dumpers |  | List individual dumpers
|  | Chutes |  | List individual chutes
| Laundry Equipment |  |  | List individual washers and dryers
| Appliances (Non household) |  |  | None
| Furniture |  |  | None
| Refrigeration Equipment |  |  | None
|  | Ice Machines |  | List individual ice machines
|  | Refrigerators (Blood & Tissue) |  | List individual refrigerators
|  | Freezers (Blood & Tissue) |  | List individual freezers
|  | Coolers (Blood & Tissue) |  | List individual coolers
| Vehicles |  |  | List individual vehicles
Fire Protection |  |  |  | None
| Fire Alarm |  |  | None but include fire alarm specifications (e.g., make, manufacturer)
| Fire Suppression |  |  | None
|  | Kitchen Hood Fire Suppression |  | List individual fire suppression systems
|  | Sprinkler Systems (Fire) |  | List individual sprinkler systems
| Fire Extinguishers |  |  | None
Elevators |  |  |  | None
| Elevators (Passenger) |  |  | List individual elevators
| Elevators (Service) |  |  | List individual elevators
| Dumbwaiters |  |  | List individual dumbwaiters
Medical Gas & Vacuum System |  |  |  | None
| Medical Gas Systems |  |  | None
|  | Medical Air System |  | List individual components (e.g., compressors, manifolds, pumps, etc.)
|  | Alarm Panels (Medical Gas) |  | None
|  |  | Master Panel | List individual panels
|  |  | Zone Panels | List individual panels
|  | Oxygen |  | None
|  |  | Outlets | List individual outlets
|  |  | Piping | None
|  |  | Valves | List individual valves
|  |  | Regulators | List individual regulators
|  | Carbon Dioxide |  | None
|  |  | Piping | None
|  |  | Manifold | List individual manifolds
|  | Nitrogen |  | List individual components (e.g., compressors, manifolds, pumps, etc.)
|  |  | Piping | None
|  |  | Outlets | List individual outlets
|  | Liquid Nitrogen |  | List individual components (e.g., compressors, manifolds, pumps, etc.)
|  |  | Piping | None
|  |  | Keep Fill Valves | List individual valves
|  | Nitrous Oxide |  | List individual components (e.g., compressors, manifolds, pumps, etc.)
|  |  | Outlets | List individual outlets
|  | Lab Air System |  | List individual components (e.g., compressors, manifolds, pumps, etc.)
| Medical Vacuum System |  |  | List individual components (e.g., compressors, manifolds, pumps, etc.)
Plumbing |  |  |  | None
| Plumbing Fixtures (Toilets, Urinals, Sinks, Tubs, Showers) |  |  | None
|  | Eye Wash Stations |  | List individual eye wash stations
|  | Tubs (Century) |  | List individual century tubs
|  | Tubs (Other) |  | None
|  | Shower (Safety) |  | List individual safety showers
|  | Filters |  | List individual filters
| Plumbing Hardware (Taps, Faucets, Flush Handles) |  |  | None
| Domestic Hot Water |  |  | List all DHW assets here organized by system and flow of DHW
|  | Heat Exchangers |  | List individual heat exchangers
| Domestic Cold Water |  |  | List all DCW assets here organized by system and flow of DCW
|  | Backflow Preventers |  | List individual backflow preventers here
|  | Sanitary Drainage |  | List all sanitary drainage assets here organized by system and flow of sewer
| Storm Drainage |  |  | List all storm drainage assets here organized by system and flow of sewer
Electrical |  |  |  | None
| Electrical Distribution System |  |  | None
|  | Main Distribution |  | List main elec distribution assets based on flow of electricity (see sample)
|  | Vital Distribution |  | List vital elec distribution assets based on flow of electricity (see sample)
|  | Delayed Vital Distribution |  | List delayed vital elec distribution assets based on flow of electricity (see sample)
|  | Conditional Distribution |  | List conditional elec distribution assets based on flow of electricity (see sample)
| Lighting (Lamps) |  |  | None
| Emergency Power |  |  | List individual emergency power assets organized by system (e.g., by generator)
| Uninterrupted Power System |  |  | List individual UPS
Communications |  |  |  | None
| Security Alarms |  |  | Create an asset for the security alarm as a whole and make it a child to this asset
| Computer Network (Cables) |  |  | None
| Nurse Call System (Call Lights, Call Bells, Call Buttons) |  |  | Create an asset for the nurse call as a whole and make it a child to this asset
| Overhead Voice Paging |  |  | None
| Satellite Dish |  |  | None
| Communication System |  |  | None
| Patient Wandering System |  |  | Create an asset for the patient wandering system as a whole and make it a child to this asset
| Security System |  |  | Create an asset for the security alarm as a whole and make it a child to this asset
| Audio Video Systems |  |  | None
| Telephone System |  |  | None
| Emergency Lighting |  |  | List individual emergency lighting packs
Heating, Ventilation & Air Conditioning |  |  |  | None
| Building Automation System |  |  | None
|  | BAS Network |  | None
|  | BAS Field Devices |  | List individual field devices
| Heating Water System |  |  | Include all heating water systems here - organize assets by system and based on the flow of the heating water
|  | Heating Water Chemical Treatment |  | None
|  | Heating Water Expansion Tanks |  | List individual tanks under each system
|  | Heating Water Circulating Pumps |  | List individual pumps under each system
|  | Heat Exchangers |  | List individual heat exchangers under each system
| Glycol Heating Systems |  |  | Include all glycol heating systems here - organize assets by system (e.g., driveway glycol system, heliport glycol system)
| Chilled Water System |  |  | Include all chiller systems here - organize assets by system (e.g., Chiller System 1; include chiller and associated cooling tower).
|  | Chillers |  | List individual chillers with associated equipment beneath each chiller (follow the flow of the chilled water)
|  | Chilled Water Chemical Treatment System |  | None
|  | Chilled Water Piping |  | None
|  | Chilled Water Expansion Tanks |  | List individual tanks under each system
|  | Chilled Water Circulating Pumps |  | List individual pumps under each system
|  | Condenser Water Circulating Pumps |  | List individual pumps under each system
| Air Handling Systems |  |  | Include all air handling systems here - organize assets by system (e.g., Air Handling System 1). See HVAC sample.
| Air Conditioning Units (Stand alone systems & DX Units) |  |  | List individual air conditioning units
| Controlled Pressure Rooms |  |  | List individual controlled pressure rooms
| Exhaust Systems |  |  | None
|  | Anesthetic Exhaust Fans |  | List individual fans organized by system
|  | Vented Bio Safety Cabinet Fans |  | List individual fans organized by system
|  | ETO Exhaust Fan |  | List individual fans organized by system
|  | Primary Shaft Exhaust Fans |  | List individual fans organized by system
|  | Isolation Room Exhaust |  | List individual assets organized by system
|  | Washroom Exhaust |  | List individual fans
| Fume Exhaust |  |  | List individual assets organized by system
| Heat Recovery |  |  | List individual assets organized by system
| Stairwell Pressurization Fan System |  |  | List individual fans
| Control Air |  |  | List individual assets organized by system
| Supply Air |  |  | If separate, feeding more than one air handling system, list supply air system assets here.
| Misc. Supply / Exhaust Fans |  |  | If separate from Air Handling Systems, include the exhaust fans here
Steam Distribution and Condensate Return |  |  |  | None
| Steam Distribution System |  |  | Isolation Valve is boundary between site and building; isolation valve is on the building side
|  | 150 PSI System |  | None
|  |  | Isolation Valves | List individual valves
|  |  | Steam Distribution Piping | None
|  |  | Safety Relief Valves | List individual valves
|  |  | Pressure Regulators | List individual regulators
|  |  | Steam Pipe Expansion Joints | None (Captured at Site Level)
|  | 60 PSI System |  | None
|  |  | Isolation Valves | List individual valves
|  |  | Steam Distribution Piping | None
|  |  | Safety Relief Valves | List individual valves
|  |  | Pressure Regulators | List individual regulators
|  | 45 PSI System |  | None
|  |  | Isolation Valves | List individual valves
|  |  | Steam Distribution Piping | None
|  |  | Safety Relief Valves | List individual valves
|  |  | Pressure Regulators | List individual regulators
|  | 15 PSI System |  | None
|  |  | Isolation Valves | List individual valves
|  |  | Steam Distribution Piping | None
|  |  | Safety Relief Valves | List individual valves
|  |  | Pressure Regulators | List individual regulators
| Condensate System |  |  | None
|  | Condensate Piping |  | None
|  | Condensate Pipe Expansion Joints |  | None (Captured at Site Level)
|  | Steam Traps |  | None
Heating Plant |  |  |  | None
| Boiler System |  |  | Break out each boiler system including all assets under their associated boiler (see boiler sample)
|  | Boilers |  | List individual boilers and break out assciated equipment under it
|  |  | Boiler Control Instruments | List individual boiler control instruments
|  |  | Boiler Header Line | List individual boiler header lines
|  |  | Burner Management Control Panel | List individual burner management control panels
|  |  | Forced Draft Fan System | List individual forced draft fans
|  |  | Fuel System | List individual fuel systems
|  |  | Feedwater Train | List individual feedwater trains
|  |  | Economizer Feedwater Heater | List individual economizers
|  |  | Steam Drum | List individual steam drums
Grounds |  |  |  | None
| Irrigation Systems |  |  | List individual irrigation systems
| Roads & Paving |  |  | None
| Landscaping |  |  | None

## 5. Elec Hierarchy Sample
Electrical Distribution System
Main Distribution
Isolation Switch (12 kV)
Main Load Circuit Breaker (12 kV)
Load Break Switch (12kV) Transformer #1
Transformer (Dry) 12400 / 600V Conditional (TX-1)
Main Breaker (600 V) Delayed Vital (Transformer 1)
Main Tie Breaker (600 V)
Vital Distribution
Distribution Sub-Panel (600V) Vital (2V-1)
Distribution Panel, 250 A, 600 V, Fed from 2V1 (A08-6)
1D-3 Breaker Enclosure 200 A, 600V, Fed from Panel A08-6
Transformer (Dry) 112.5 kVA 600V ~ 208V/120V Vital
Distribution Panel, 408A, 120V/208V, Vital (A-09)
Panelboard, 208V, Vital, Fed from A-09 (A40)
Panelboard, 208V, Vital, Fed from A-09 (A40A)
Panelboard, 208V, Vital, Fed from A-09 (A41)
Delayed Vital Distribution
Conditional Distribution

## 6. Boiler Hierarchy Sample
Steam Generation
Blr. #1 - High Pressure Boiler (750) - HP58228
Blr.#1 - Boiler Control Instruments
Blr.#1 - O2 Analyzer
Blr.#1 - Boiler Header Line
Blr.#1 - Superheater Safety Valve, 1 1/2", 700 psi
Blr.#1 - Burner Management Control Panel
Blr.#1 - Forced Draft Fan System
Blr.#1 - Damper - Forced Draft Fan
Blr.#1 - Drive - Forced Draft Fan
Blr.#1 - Fan - Forced Draft
Blr.#1 - Motor - Forced Draft Fan
Blr.#1 - Fuel System
Blr.#1 - Gas Fuel Train
Blr.#1 - Gas Control Valve
Blr.#1 - Gas Control Valve Actuator
Blr.#1 - Gas Control Valve Positioner
Blr.#1 - Oil Fuel Train
Blr.#1 - Oil Control Valve
Blr.#1 - Oil Control Valve Actuator
Blr.#1 - Oil Control Valve Positioner
Blr.#1 - Feedwater Train
Blr.#1 - Control Valve - Feedwater
Blr.#1 - Bypass Isolating Valve - Feedwater Control
Blr.#1 - Inlet Isolating Valve - Feedwater Control Station
Blr.#1 - Outlet Isolating Valve - Feedwater Control Station
Blr.#1 - Economizer Feedwater Heater
Economizer- Safety Valve, 3/4" : 600PSI
Blr.#1 - Steam Drum
Blr.#1 - Safety Valve #2, 1 1/2 ": 745 PSI
Blr.#1 - Water Column
Blr #1- Safety Valve #1, 1 1/2": 750 PSI

## 7. HVAC Hierarchy Sample
Air Handling Systems
Air Handling System AHU#1
General Exhaust Fan, EF-1A
Variable Speed Drive, VSD - EF1A
Washroom Exhaust Fan, EF-1B
Variable Speed Drive, VSD - EF1B
Return Air Fan, RF-1
Variable Speed Drive, VSD - RF1
Smoke Exhaust Fan, EF-1C
Supply Fan, SF-1A
Variable Speed Drive, VSD - SF1A
Supply Fan, SF-1B
Variable Speed Drive, VSD - SF1B
Booster Fan, BF-G536
Humidifier, HU-1A
Humidifier, HU-1B